United Nations Population Fund,

UNFPA Yemen

Haddah St. behind Lazourde Hotel

Sanaa’a.,Yemen

Tel: +967 1 433160

Website: www.unfpa.org

Email:procurement.yemen@unfpa.org

Date: 28/06/2026

Request for Quotation No. YEM/2026/002

Provision of Generators for UNFPA

Dear Sir/Madam,

We hereby solicit your quotation for the supply of Generators and fuel tank for UNFPA- Aden office, as per the technical specifications detailed in Annex I and II of this RFQ.

The items are to be delivered to Aden as within three weeks from PO issuance.  The quotation shall be valid at least for 3 months after the closing date.

If you are interested in submitting a quotation for these services, kindly fill in the attached Quotation Form or your Company form and send by E-mail only to the address indicated below not later than 13/07/2026, 14:00 (Aden time):

Email: procurement.yemen@unfpa.org

Bidders must enter the following text in the email subject line:

RFQ/YEM/2026/002- Generator

Please submit your quotation in US Dollars currency. Conversion of currency into the UNFPA preferred currency, if the offer is quoted differently from what is required, should be based only on UN Operational Exchange Rate prevailing at the time of competition deadline.

For any technical inquiries, please contact al-hakimi@unfpa.org

Bidders should NOT submit any Bid to this contact or your Bid will be declared invalid, as UNFPA will not able to guarantee the confidentiality of the Bidding process.

Bidders may request clarifications not later than 09 July 2026, 14:00 Aden time.

Quotations submitted by email must be free from any form of virus or corrupted contents, or the quotations shall be rejected.

It shall remain your responsibility to ensure that your quotation will reach the address above on or before the deadline. Quotations that are received by UNFPA after the deadline indicated above, for whatever reason, shall not be considered for evaluation. Kindly ensure that it is signed and in the .PDF format, and free from any virus or corrupted files.

Please take note of the following requirements and conditions pertaining to the supply of the above mentioned goods:

Partial quotes - Not Permitted

Partial delivery – Not Permitted

Alternative Bids are not accepted under this RFQ. In the event of a supplier submitting more than one bid, the following shall apply:

- All bids marked alternative will be rejected and only the base will be evaluated;

- All bids will be rejected if no indication is provided as to which bids are alternative bids.

Bidders may modify their offers in writing prior to the submission deadline. The bidder must submit the proposed modification via email that must be clearly marked as “MODIFICATION”.

In this case, the previous offer will be declined and the modified offer shall be considered for the evaluation process.  Also, if the same bidder has submitted several offers before the bid deadline superseding each other only the last received offer will be considered for opening and further evaluation.

Note: Current UNFPA supplier policies apply to this solicitation and can be found at: http://www.unfpa.org/suppliers.

Documents to be submitted with the bid:

- Duly Completed and Signed Bid Submission Form

- Duly Completed and Signed Financial bid form

- Duly Completed – Delivery Schedule Form

- Evidence of previous experience in a similar field and with the same type of requirements: list of major contracts completed within the last three years with national, international organizations, including UN.

- Latest Business Registration Certificate, (please note that all registration documents and licenses must be valid);

- Latest Internal Revenue Certificate / Tax Clearance;

Best regards,

UNFPA

Yemen

Quotation Form

Name of Bidder:

Date of Bid:

Request for Quotation No:

Currency of Bid price:

Delivery time (weeks from receipt of order till dispatch):

Expiration of Validity of Quotation (The quotation shall be

valid for a period of at least 3 months after the Closing date.):

Price Schedule:

| Item No. | ## Quantity | Transportation cost to port of Destination (specify mode of trp.) | Total CPT/CFR (Destination port) | Delivery schedule (months) |
| --- | --- | --- | --- | --- |

In your offer, please include:

- Specific technical specifications of products offered

- Quality standard of the products

# Vendor’s Comments:

I hereby certify that this company, which I am duly authorized to sign for, accepts the terms and conditions of UNFPA (http://www.unfpa.org/resources/unfpa-general-conditions-contract ) and we will abide by this quotation until it expires.

Name and title								Date and Place

Annex I

### Technical Specifications and Requirements

The offered generator must meet or exceed the following minimum technical specifications:

#### A. Generator Set Specifications

- Capacity (Prime Power): Minimum 60 kVA (48 kW) continuous prime rating under standard operational conditions.

- Phase/Voltage: 3-Phase, 4-Wire / voltage 380/220V.

- Frequency: 50 Hz.

- Engine Type: Heavy-duty diesel engine, 4-stroke, water-cooled, direct injection.

- Alternator: Brushless, self-exciting, Class H insulation, IP23 protection (minimum).

- Enclosure: Sound-attenuated (silent) and weatherproof canopy. Anti-corrosion powder-coated steel. Maximum noise level [70-75 dB at 7 meters].

- Control Panel: Digital/Microprocessor-based control panel displaying standard parameters (voltage, frequency, oil pressure, coolant temp, battery voltage) and safety alarms/shutdowns

#### B. Accessories and Additional Requirements

- Automatic Transfer Switch (ATS): Included and compatible with the generator, appropriately sized for 60 kVA.

- Battery: Heavy-duty maintenance-free starter batteries with cables and battery charger.

- Exhaust System: Residential silencer with exhaust piping.

- Manuals: Comprehensive operation, maintenance, and spare parts manuals in English.

#### C. Warranty and Support

- Warranty: Minimum of 12 months

- After-Sales Service: Supplier must demonstrate the availability of spare parts and qualified technicians within Yemen- Aden.

- Mandatory Requirement: Equipment Origin and Authorization

- Certified Original Equipment Manufacturer (OEM): All bidding entities must be the Original Equipment Manufacturer (OEM) or a direct, certified authorized agent/distributor of the OEM. Valid certification or a Manufacturer’s Authorization Form (MAF) must be submitted with the bid.

- No Local Assembly: All generator sets must be completely factory-assembled, tested, and certified at the manufacturer's official facility. Local assembly of components or third-party packaging will not be accepted and will result in immediate disqualification of the bid.

### Delivery and Logistics

| Requirement | Details |
| --- | --- |
| Delivery Term (Incoterms 2020) | Aden Office |
| Delivery Location | Alshabat Area |
| Installation & Commissioning | Required at the delivery site, including testing under load |

### Technical Specifications and Requirements

The offered generator must meet or exceed the following minimum technical specifications:

#### A. Generator Set Specifications

- Capacity (Prime Power): Minimum 100 kVA (80 kW) continuous prime rating under standard operational conditions.

- Phase/Voltage: 3-Phase, 4-Wire / voltage 380/220V.

- Frequency: frequency 50 Hz.

- Engine Type: Heavy-duty diesel engine, 4-stroke, water-cooled, direct injection.

- Alternator: Brushless, self-exciting, Class H insulation, IP23 protection (minimum).

- Enclosure: Sound-attenuated (silent) and weatherproof canopy. Anti-corrosion powder-coated steel. Maximum noise level [70-75 dB at 7 meters].

- Control Panel: Digital/Microprocessor-based control panel displaying standard parameters (voltage, frequency, oil pressure, coolant temp, battery voltage) and safety alarms/shutdowns.

#### B. Accessories and Additional Requirements

- Automatic Transfer Switch (ATS): Included and compatible with the generator, appropriately sized for 100 kVA.

- Battery: Heavy-duty maintenance-free starter batteries with cables and battery charger.

- Exhaust System: Residential silencer with exhaust piping.

- Manuals: Comprehensive operation, maintenance, and spare parts manuals in English.

#### C. Warranty and Support

- Warranty: Minimum of 12 months

- After-Sales Service: Supplier must demonstrate the availability of spare parts and qualified technicians within Yemen- Aden.

- Mandatory Requirement: Equipment Origin and Authorization

- Certified Original Equipment Manufacturer (OEM): All bidding entities must be the Original Equipment Manufacturer (OEM) or a direct, certified authorized agent/distributor of the OEM. Valid certification or a Manufacturer’s Authorization Form (MAF) must be submitted with the bid.

- No Local Assembly: All generator sets must be completely factory-assembled, tested, and certified at the manufacturer's official facility. Local assembly of components or third-party packaging will not be accepted and will result in immediate disqualification of the bid.

### Delivery and Logistics

| Requirement | Details |
| --- | --- |
| Delivery Term (Incoterms 2020) | Aden Office |
| Delivery Location | Alshabat Area |
| Installation & Commissioning | Required at the delivery site, including testing under load |

#### A. Generator Set Specifications

- Capacity (Prime Power): Minimum 150 kVA (120 kW) continuous prime rating under standard operational conditions.

- Phase/Voltage: 3-Phase, 4-Wire / [voltage 380/220V].

- Frequency: frequency 50 Hz.

- Engine Type: Heavy-duty diesel engine, 4-stroke, water-cooled, direct injection.

- Alternator: Brushless, self-exciting, Class H insulation, IP23 protection (minimum).

- Enclosure: Sound-attenuated (silent) and weatherproof canopy. Anti-corrosion powder-coated steel. Maximum noise level [70-75 dB at 7 meters].

- Control Panel: Digital/Microprocessor-based control panel displaying standard parameters (voltage, frequency, oil pressure, coolant temp, battery voltage) and safety alarms/shutdowns.

#### B. Accessories and Additional Requirements

- Automatic Transfer Switch (ATS): Included and compatible with the generator and at least at 200 amp.

- Battery: Heavy-duty maintenance-free starter batteries with cables and battery charger.

- Exhaust System: Residential silencer with exhaust piping.

- Manuals: Comprehensive operation, maintenance, and spare parts manuals in English.

#### C. Warranty and Support

- Warranty: Minimum of 12 months.

- After-Sales Service: Supplier must demonstrate the availability of spare parts and qualified technicians within Yemen- Aden.

- Mandatory Requirement: Equipment Origin and Authorization

- Certified Original Equipment Manufacturer (OEM): All bidding entities must be the Original Equipment Manufacturer (OEM) or a direct, certified authorized agent/distributor of the OEM. Valid certification or a Manufacturer’s Authorization Form (MAF) must be submitted with the bid.

- No Local Assembly: All generator sets must be completely factory-assembled, tested, and certified at the manufacturer's official facility. Local assembly of components or third-party packaging will not be accepted and will result in immediate disqualification of the bid.

### Delivery and Logistics

| Requirement | Details |
| --- | --- |
| Delivery Term (Incoterms 2020) | Aden Office |
| Delivery Location | Alshabat Area |
| Installation & Commissioning | Required at the delivery site, including testing under load |

Annex II

# Technical Specifications for the Fabrication of Diesel Storage Tanks

## 1. Scope of Work

This specification covers the design, engineering, materials, fabrication, testing, and delivery of two (2) carbon steel diesel storage tanks:

- Item 01: 6,000 – 7,000 Liter Underground Storage Tank with 6mm thickness

- Item 02: 1,500 – 2,000 Liter Elevated Gravity-Feed Storage Tank with 6mm thickness

## 2. Technical Data & Dimensions

### Item 01: 6,000 – 7,000 Liter Tank

- Nominal Capacity: ~6,800 Liters

- Orientation: Vertical Cylindrical shape

- Shell Thickness: 6.0 mm (Minimum)

- End Plates: Dished heads, 6.0 mm thickness

- Access Hatch: 600 mm × 600 mm square extension window (manway collar) mounted on top centerline. Height of collar: 200 mm above shell. Complete with 6mm/8mm blind flange lid, Nitrile/Viton fuel-resistant gasket, and heavy-duty zinc-plated securing bolts.

- Structural Reinforcement: Reinforcing pad (doubled plate) required around the 600 mm × 600 mm cutout base.

### Item 02: 1,500 – 2,000 Liter Elevated Tank

- Nominal Capacity: ~1,920 Liters

- Orientation: Horizontal Square

- Shell Thickness: 6.0 mm (Minimum)

- End Plates: Dished heads, 6.0 mm thickness

- Access Hatch: 600 mm × 600 mm square extension window (manway collar) mounted on top centerline. Height of collar: 200 mm above shell. Complete with 6mm/8mm blind flange lid, fuel-resistant gasket, and securing bolts.

- Support Structure:

  - Two (2) curved steel saddles (minimum 120-degree wrap) welded to the tank shell with wear/doubled plates.

  - Four (4) structural columns to elevate the bottom of the tank shell.

  - Heavy-duty cross-bracing (minimum 50mm × 50mm × 5mm angle iron) on all four sides of the frame.

## 3. Materials & Fabrication Requirements

- Steel Grade: Mild Carbon Steel

- Welding Standards: All welding must be performed by welders in accordance with recognized standards. Full-penetration butt welds are required for all major shell seams.

- Nozzles & Connections (Per Tank):

  - 1 × 2" BSP/NPT Female Threaded Socket for Fill Pipe

  - 1 × 2" BSP/NPT Female Threaded Socket for Vent (with vent cap)

  - 1 × 1" BSP/NPT Female Threaded Socket for Suction/Outlet

  - 1 × 1" BSP/NPT Female Threaded Socket for Dipstick/Level Gauge

  - 1 × 1" Drain plug located at the lowest bottom point of the shell.

  - Note: Nozzles may be integrated onto the 600x600mm manway lid or placed directly on the shell top.

- Lifting Lugs: Minimum of two (2) heavy-duty lifting lugs welded to the top of each tank shell, rated to safely lift the empty tank weight.

- Earthing: One (1) dedicated stainless steel grounding/earthing lug welded near the base frame of each tank.

## 4. Testing & Inspection

- Pressure/Leak Testing: Prior to painting and delivery, each tank must undergo a pneumatic leak test (air-and-soap test) at a minimum of 0.3 to 0.5 bar, or a hydrostatic test, held for a minimum of 2 hours.

## 5. Surface Preparation & Coating

- External Surface: Commercial sandblasting (SSPC-SP6 or Sa 2.5) followed immediately by:

  - One (1) coat of anti-corrosive red oxide zinc-chromate primer.

  - Two (2) coats of premium glossy polyurethane or enamel exterior paint (Color: Industrial Gloss White or Signal Yellow, UV-resistant).

- Internal Surface: Cleaned thoroughly, free of welding slag, rust, or debris, and treated with a light coating of soluble rust-preventative oil compatible with diesel fuel.

Note:

Piping job will be decided after the verification site visit